Proposed IEA BESTEST Multi-Zone Conduction Cases

IEA: SHC Task 34 / ECBCS Annex 43

May 2004

By

Joel Neymark

J. Neymark & Associates

Golden, Colorado, U.S.

Ron Judkoff

National Renewable Energy Laboratory

Golden, Colorado, U.S.

Table of Contents

Page

Introduction                           	 3

Case MZ200: 2-Zone Steady-State Analytical Verification Base Case 	 5

Case MZ210: 2-Zone Steady-State Conduction with Interior Infrared Radiation Exchange 	 10

Case MZ300: 3-Zone Steady-State Analytical Verification Base Case	 11

Case MZ310: 3-Zone Steady-State with Internal Gains in Zone C 	 14

References                             	 15

Appendix A – TMY2 File Format	 16

Introduction

A method of test for evaluating building energy simulation computer programs – International Energy Agency Building Energy Simulation Test and Diagnostic Method (IEA BESTEST) - was developed by International Energy Agency (IEA) Solar Heating and Cooling Programme (SHC) Task 12 (Judkoff and Neymark, 1995).  A new task that continues IEA’s work on testing and validation of building energy simulation tools is jointly sponsored by both SHC and the Energy Conservation in Buildings and Community Systems (ECBCS) programmes as IEA SHC Task 34 / Annex 43.  One objective of IEA SHC Task 34 / ECBCS Annex 43 is to extend the original IEA BESTEST to include additional test cases for multi-zone heat transfer.

New test cases – summarized in Table 1 – are designed for testing the ability of building energy analysis tools to model multi-zone heat transfer.  The test cases involve: comparing simulation results to analytical solutions (analytical verification), and comparing simulation results to each other (comparative tests).

### Accompanying Electronic Files

The following TMY2-format weather data file is included with the accompanying electronic media:

MZDUMMY.TM2.

For reporting output use the following file provided with the accompanying electronic media:

MZ-Output.XLS.

Participants must submit modeler reports with their simulation results.  For modeler reports, use the format according to the following file provided with the accompanying electronic media:

MZ-ModRep.DOC.

### Table 1.  Multi-Zone Steady-State Conduction Test Case Summary

Case MZ200: 2-Zone Steady-State Analytical Verification Base Case

Objective

Test the ability of whole-building energy simulation software to model steady-state interzonal conduction for two zones.

# Method

This case isolates multi-zone conduction by utilizing a 2-zone building with an adiabatic exterior shell and a thermally conductive internal dividing wall.  Cooling loads are generated with internal gains.  Interzonal heat transfer is driven by different temperature set points in each zone.  Additional simplifications include constant interior surface convective coefficients, and disabled radiation exchange (interior surface emittance = 0).  Because most whole-building simulation programs require weather data for generating results, dummy weather data (TMY2-format) is provided.  Compare whole-building simulation results to analytical solution.

# Specification

The bulk of the work for implementing the remaining cases is assembling an accurate base building model.  It is recommended to thoroughly check base building inputs and results before going on to the other cases.

Case MZ200 is summarized in Figure MZ200-1.   Input parameters are described below.

Figure MZ200-1: Case MZ200 – Plan View

## Building  Construction

- Zone plan dimensions each zone  = 6 m (19.685 ft) by 8 m (26.247 ft), see Figure MZ200-1.

- Zone height = 2.7 m (8.858 ft).

- Air volume of each zone = 129.6 m3 (4577 ft3)

- The internal wall common to and separating Zone A from Zone B has material properties as described in Tables MZ200-1a and MZ200-1b using SI and IP units respectively; IP units were developed using conversions of ASHRAE (2001).

- Internal wall dimensions: length = 8 m (26.247 ft), height = 2.7 m (8.858 ft), thickness = 0.15 m (0.4921 ft)

- All external surfaces of the zones including exterior walls, floor, and roof are adiabatic (thermal conductance = 0 W/m2K); if your software does not allow adiabatic surfaces, use the lowest thermal conductance your software allows (e.g. 0.000001 W/m2K)

- All external surfaces are massless; if your software does not allow massless surfaces, use the lowest density and/or thermal capacitance that your software allows (e.g. 0.000001 kg/m3 and/or J/kgK)

- There is no interior or exterior surface radiation exchange; one possible method to disable radiation exchange is to set interior and exterior solar absorptances and infrared emittances to 0, or as low as your software allows (e.g. 0.000001)

- No windows

- No infiltration or ventilation

Table MZ200-1a: Common Wall Material Properties – SI Units

Table MZ200-1b: Common Wall Material Properties – IP Units

## Internal Gains

- Zone A: 1000 W  (3412 Btu/h)

- Zone B: 1000 W  (3412 Btu/h)

- Internal gains are 100% convective, 0% radiative

- Internal gains are 100% sensible, 0% latent

These are internally generated sources of heat (from equipment, lighting, occupants, etc.) that are not related to operation of mechanical space cooling equipment.

## Convective Surface Coefficients

- Common wall interior convective surface coefficient = 4 W/m2K (0.7045 Btu/hft2°F), applied to both sides of the wall (see Tables MZ200-1a and MZ200-1b)

- Adiabatic wall interior convective surface coefficients = 4 W/m2K (0.7045 Btu/hft2°F)

- Exterior convective surface coefficients = 0 W/m2K, or as low as your software allows.

## Mechanical System

The mechanical system provides sensible cooling only (no heating), and is ideal.  The purpose of the cooling system is to give results for energy consumption that are equal to the sensible cooling load.  Model the cooling system as closely as your software allows, as follows:

- Set points

  - Zone A: Cool = ON if temperature > 25°C (77°F); otherwise Cool = OFF.     Heat = always OFF

  - Zone B: Cool = ON if temperature > 15°C (59°F); otherwise Cool = OFF.     Heat = always OFF

- Sufficient (or greater) capacity to maintain the zone air temperature set point; for example, 1000 kW (3412 kBtu/hft2F)

- Uniform (well mixed) zone air temperature

- 100% efficiency (COP = 1)

- 100% convective air system

- Ideal controls (zone always at set point); for example, assume the heat addition rate equals the equipment capacity (non-proportional control) and there is continuous ON/OFF cycling within the hour as needed

- Thermostat sensing only the zone air temperature

- There is no moisture (latent heat) removal.

Weather Data

Weather data is arbitrary because the building shell is adiabatic.  If your software requires weather data to perform a simulation, use as dummy data the TMY2-format weather data provided with the file:

“MZDUMMY.TM2”.

#### TMY2 weather data format is described in Appendix A.  A summary of site and weather data parameters is given in Table MZ200-2.  This weather data file is based on Miami.TM2, but includes many data elements set to 0 or approximate lower limits, and other data elements set to neutral (non-extreme) constant values as follows:

- Global horizontal, direct normal, and diffuse horizontal radiation and illuminance all set to 0 (extraterrestrial horizontal and direct normal radiation were left unchanged from the original weather data file)

- Total and opaque sky cover = 10 tenths, implying the entire sky dome is covered by clouds; this setting intended to reduce exterior infrared radiation exchange

- Dry-bulb temperature = 20°C (is the average of the zone temperatures for Case MZ200)

- Dew-point temperature = -56.6°C (corresponds with humidity ratio of 0.000007 kg/kg and standard atmospheric pressure); calculation of dew point temperature applies common psychrometric formulae (ASHRAE, 2001; Brandemuehl, 1993).  TMY2 documentation indicates that -60°C is the lower limit for TMY2 data.

- Relative humidity = 0.05% (corresponds with humidity ratio of 0.000007 kg/kg, standard atmospheric pressure, and given dry-bulb temperature); calculations apply common psychrometric formulae (ASHRAE, 2001; Brandemuehl, 1993).  This value rounds to 0% in the weather data.

- Atmospheric pressure = 1013 millibars (= standard atmosphere of 14.696 psia)

- Wind speed = 0 m/s

- Visibility = 20 km (rough annual average for Miami and Denver)

- Ceiling height = 2000 m (rough annual average for Miami and Denver)

- Present weather: no rain, hail, etc.

- Precipitable water = 0 mm

- Aerosol optical depth = 0.1 broadband turbidity (rough annual average of Miami and Denver)

- Snow depth = 0 cm, with ≥ 88 days since last snowfall.

#### Table MZ200-2. Site and Weather Summary for Multi-Zone Conduction Tests—TMY2 Data

| Weather Type | Artificial Conditions |
| --- | --- |
| Weather Format | TMY2 |
| Latitude | 25.8° North |
| Longitude (local site) | 80.3° West |
| Altitude | 2 m (6.6 ft) |
| Time Zone (Standard Meridian Longitude) | 5 (75° West) |
| Site | Flat, unobstructed, located exactly at weather station |
| Mean Ambient Dry-Bulb Temperature (constant) | 20°C (68°F) |
| Dew Point Temperature (constant) | -56.6°C (-69.9°F) |
| Humidity Ratio (constant) | 0.000007 kg moisture/kg dry air (0.000007 lb moisture/lb dry air) |
| Relative Humidity (constant) | 0.05% |
| Mean Annual Wind Speed | 0.0 m/s (0.0 miles/h) |
| Maximum Annual Wind Speed | 0.0 m/s (0.0 miles/h) |
| Global Horizontal Solar Radiation Annual Total | 0 MJ/m² (0 kBtu/ft²) |
| Direct Normal Solar Radiation Annual Total | 0 MJ/m² (0 kBtu/ft²) |
| Diffuse Horizontal Solar Radiation Annual Total | 0 MJ/m² (0 kBtu/ft²) |

#### Output requirements

- Steady state cooling load in Zone A (qA) in W or Wh/h

- Steady state cooling load in Zone B (qB) in W or Wh/h

- Air temperature in Zone A (TA) (°C)

- Air temperature in Zone B (TB) (°C)

Run the simulations for 1 year and submit values for the last hour of the year.

## Analytical solution

Based on Figure MZ200-1, a First Law steady-state energy balance yields the following:

qA = qint – UA (TA – TB)

and

qB = qint + UA (TA – TB)

where:

qA ≡ cooling load in Zone A, Watts

qB ≡ cooling load in Zone B, Watts

qint ≡ internal gains in Zone A and Zone B, Watts

UA ≡ internal wall conductance = 1.6 W/m2K * 2.7 m * 8 m = 34.56 W/K

TA ≡ air temperature in Zone A, °C

TB ≡ air temperature in Zone B, °C

For: TA = 25°C, TB = 15°C, qint = 1000 W, implies

qA =   654.4 W  (2233 Btu/h)

qB = 1345.6 W  (4591 Btu/h).

Case MZ210: 2-Zone Steady-State Conduction with Interior Infrared Radiation Exchange

Objective

Test the effect of interior infrared radiation exchange on interzonal conduction.

# Method

This case is similar to MZ200, but isolates the effect of interior infrared radiation exchange by setting interior emittance to 0.9 for all interior surfaces.  Compare whole-building simulation results to each other.  Comparison of results for MZ210 versus MZ200 (MZ210-MZ200) checks the sensitivity to interior infrared radiation exchange.

# Specification

This case is exactly as MZ200 except for the following.

- Interior surface infrared emittance (ε) = 0.9.  This value applies to the both sides of the internal common wall, and also to the interior sides of the adiabatic walls.  If your software allows direct input of surface infrared emittance then ignore the following paragraph.

If your software does not explicity model internal radiation exchange, radiation exchange may be approximated with a surface coefficient of 5.13 W/m2K (0.9035 Btu/hft2F).  (ANSI/ASHRAE 2001)   If a surface coefficient adjustment is applied for this purpose, then for the internal common wall radiative exchange and convection are occurring in parallel, so that the total combined convective/radiative surface heat transfer coefficient for the internal common wall is 9.13 W/m2K (1.608 Btu/hft2F).

#### Output requirements

- See Case MZ200

- Steady-state interior surface temperatures for floor, ceiling, north wall, east wall, west wall, and south wall in each zone; these are average temperatures over the area of the given surface.

Run the simulations for 1 year and submit values for the last hour of the year.

Case MZ300: 3-Zone Steady-State Analytical Verification Base Case

Objective

Test the ability of whole-building energy simulation software to model steady-state interzonal conduction for three zones with: internal gains in all zones, temperature controlled in Zone A and Zone B, and temperature floating in Zone C.

# Method

This case isolates multi-zone conduction by utilizing a 3-zone building with an adiabatic exterior shell and two thermally conductive internal dividing walls.  Cooling loads are generated with internal gains.  Interzonal heat transfer is driven by different temperature set points in Zone A and Zone B, and floating zone temperature in Zone C.  Additional simplifications include constant interior surface convective coefficients, and disabled radiation exchange (interior surface emittance [ε] = 0).  Because most whole-building simulation programs require weather data for generating results, dummy weather data (TMY2-format) is provided.  Compare whole-building simulation results to analytical solution.

# Specification

This case is exactly as MZ200 except for the following.

# Zone C is added per Figure MZ300-1.

Figure MZ300-1: Case MZ300 – Plan View

## Zone C  Details

# Internal gains (Zone C) = 864 W  (2948 Btu/h)

    - Internal gains are 100% convective, 0% radiative

    - Internal gains are 100% sensible, 0% latent

    - These are internally generated sources of heat (from equipment, lighting, occupants, etc.) that are not related to operation of mechanical space cooling equipment

  - Zone plan dimensions = 6 m (19.685 ft) by 8 m (26.247 ft), see Figure MZ300-1.

  - Zone height = 2.7 m (8.858 ft).

  - Air volume = 129.6 m3 (4577 ft3)

# Material properties and dimensions for both internal walls are the same as for Case MZ200, see Tables MZ200-1a and MZ200-1b

  - All external surfaces of the zone including exterior walls, floor, and roof are adiabatic (thermal conductance = 0 W/m2K); if your software does not allow adiabatic surfaces, use the lowest thermal conductance your software allows (e.g. 0.000001 W/m2K)

  - All external surfaces are massless; if your software does not allow massless surfaces, use the lowest density and/or thermal capacitance that your software allows (e.g. 0.000001 kg/m3 and/or J/kgK)

  - There is no interior or exterior surface radiation exchange; one possible method to disable radiation exchange is to set interior and exterior solar absorptances and infrared emittances to 0, or as low as your software allows (e.g. 0.000001)

  - No windows

  - No infiltration or ventilation

## Convective Surface Coefficients

    - Common wall interior convective surface coefficient = 4 W/m2K (0.7045 Btu/hft2°F), applied to both sides of both walls

    - Adiabatic wall interior convective surface coefficients = 4 W/m2K (0.7045 Btu/hft2°F)

    - Exterior convective surface coefficients = 0 W/m2K, or as low as your software allows.

  - There is no cooling or heating for Zone C; the Zone C temperature is allowed to float to equilibrium.

#### Output requirements

- Steady state cooling load in Zone A (qA), W or Wh/h

- Steady state cooling load in Zone B (qB), W or Wh/h

- Air temperature in Zone A (TA), °C

- Air temperature in Zone C (TC), °C

- Air temperature in Zone B (TB), °C

Run the simulations for 1 year and submit values for the last hour of the year.

# Analytical solution

For Case MZ300, a First Law steady-state energy balance yields the following:

qA = qint + UA (TC – TA)								[MZ300-1]

qB = qint + UA (TC – TB)								[MZ300-2]

qC = 0 = qintC – UA (TC – TA) – UA (TC – TB) 					[MZ300-3]

where:

qA ≡ cooling load in Zone A, Watts

qB ≡ cooling load in Zone B, Watts

qC ≡ cooling load in Zone C, Watts

qint ≡ internal gains in Zone A and Zone B, Watts

qintC ≡ internal gains in Zone C, Watts

UA ≡ internal wall conductance = 1.6 W/m2K * 2.7 m * 8 m = 34.56 W/K

TA ≡ air temperature in Zone A, °C

TB ≡ air temperature in Zone B, °C

TC ≡ air temperature in Zone C, °C

From Eqn. MZ320-3, TC = (qintC /UA + TA + TB)/2				[MZ300-3a]

For: TA = 25°C, TB = 15°C, qintC = 864 W, Equation MZ300-3a implies:

TC = 32.5°C.

From the remaining equations, and for qint = 1000 W:

qA = 1259.2 W  (4296 Btu/hft2F)

qB = 1604.8 W  (5475 Btu/hft2F).

Case MZ310: 3-Zone Steady-State Conduction with Interior Infrared Radiation Exchange

Objective

Test the effect of interior infrared radiation exchange on interzonal conduction with three zones and two common walls.

# Method

This case is similar to MZ300, but isolates the effect of interior infrared radiation exchange by setting interior emittance to 0.9 for all interior surfaces.  Compare whole-building simulation results to each other.  Comparison of results for MZ310 versus MZ300 (MZ310-MZ300) checks the sensitivity to interior infrared radiation exchange.

# Specification

This case is exactly as MZ300 except for the following.

- Interior surface infrared emittance (ε) = 0.9.  This value applies to the both sides of the internal common wall, and also to the interior sides of the adiabatic walls.  If your software allows direct input of surface infrared emittance then ignore the following paragraph.

If your software does not explicity model internal radiation exchange, radiation exchange may be approximated with a surface coefficient of 5.13 W/m2K (0.9035 Btu/hft2F).  (ANSI/ASHRAE 2001)   If a surface coefficient adjustment is applied for this purpose, then for the internal common wall radiative exchange and convection are occurring in parallel, so that the total combined convective/radiative surface heat transfer coefficient for the internal common wall is 9.13 W/m2K (1.608 Btu/hft2F).

#### Output requirements

- See Case MZ300

- Steady-state interior surface temperatures for floor, ceiling, north wall, east wall, west wall, and south wall in each zone; these are average temperatures over the area of the given surface.

Run the simulations for 1 year and submit values for the last hour of the year.

References

ASHRAE, 2001 Handbook of Fundamentals, American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, GA.  See Chp. 37 regarding conversion factors; see Chp. 6 regarding psychrometrics.

ANSI/ASHRAE Standard 140-2001, Standard Method of Test for the Evaluation of Building Energy Analysis Computer Programs, American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, GA.  See Annex B5.

Brandemuehl M., 1993, HVAC 2 Toolkit, American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Atlanta, GA.  See p. 7-15.

Judkoff, R. and Neymark, J., 1995, International Energy Agency Building Energy Simulation Test (BESTEST) and Diagnostic Method, NREL/TP-472-6231, National Renewable Energy Laboratory, Golden, CO.  Download address: http://www.nrel.gov/docs/legosti/old/6231.pdf (PDF 13.8 MB)

Marion, W. and Urban, K, 1995, User’s Manual for TMY2s, National Renewable Energy Laboratory, Golden, CO.

# Appendix AAppA.	 TMY2 File Format

This format information was taken from the TMY2 User’s Manual (Marion and Urban 1995), and can be found electronically at http://www.nrel.gov.

## Data and Format

For each station, a TMY2 file contains 1 year of hourly solar radiation, illuminance, and meteorological data. The files consist of data for the typical calendar months during 1961-1990 that are concatenated to form the typical meteorological year for each station.

Each hourly record in the file contains values for solar radiation, illuminance, and meteorological elements. A two-character source and uncertainty flag is attached to each data value to indicate whether the data value was measured, modeled, or missing, and to provide an estimate of the uncertainty of the data value.

## File Header

The first record of each file is the file header that describes the station.  The file header contains the WBAN number, city, state, time zone, latitude, longitude, and elevation. The field positions and definitions of these header elements are given in Table a.1, along with sample FORTRAN and C formats for reading the header.

Table A.1 TTMY2head .	TMY2 weather file header format

| Field Position | Element | Definition |
| --- | --- | --- |
| 002 - 006 | WBAN Number | Station's Weather Bureau Army Navy number |
| 008 - 029 | City | City where the station is located (maximum of 22 characters) |
| 031 - 032 | State | State where the station is located (abbreviated to two letters) |
| 034 - 036 | Time Zone | Time zone is the number of hours by which the local standard time is ahead of or behind Universal Time. For example, Mountain Standard Time is designated -7 because it is 7 hours behind Universal Time. |
| 038 - 044 038 040 - 041 043 - 044 | Latitude | Latitude of the station N = North of equator Degrees Minutes |
| 046 - 053 046 048 - 050 052 - 053 | Longitude | Longitude of the station W = West, E = East Degrees Minutes |
| 056 - 059 | Elevation | Elevation of station in meters above sea level |
| FORTRAN Sample Format: ( 1X,A5,1X,A22,1X,A2,1X I3,1X,Al,lX,I2,1X,I2,1X,Al,lX,I3,1X,I2,2X,I4 ) C Sample Format: ( %s %s %s %d %s %d %d %s %d %d %d ) |

## Hourly Records

Following the file header, 8760 hourly data records provide 1 year of solar radiation, illuminance, and meteorological data, along with their source and uncertainty flags. Table a.2 provides field positions, element definitions, and sample FORTRAN and C formats for reading the hourly records.

Each hourly record begins with the year (field positions 2-3) from which the typical month was chosen, followed by the month, day, and hour information in field positions 4-9. The times are in local standard time (previous TMYs based on SOLMET/ERSATZ data are in solar time).

For solar radiation and illuminance elements, the data values represent the energy received during the 60 minutes preceding the hour indicated. For meteorological elements (with a few exceptions), observations or measurements were made at the hour indicated. A few of the meteorological elements had observations, measurements, or estimates made at daily, instead of hourly, intervals. Consequently, the data values for broadband aerosol optical depth, snow depth, and days since last snowfall represent the values available for the day indicated.

## Source and Uncertainty Flags

With the exception of extraterrestrial horizontal and extraterrestrial direct radiation, the two field positions immediately following the data value provide source and uncertainty flags both to indicate whether the data were measured, modeled, or missing, and to provide an estimate of the uncertainty of the data. Source and uncertainty flags for extraterrestrial horizontal and extraterrestrial direct radiation are not provided because these elements were calculated using equations considered to give exact values.

For the most part, the source and uncertainty flags in the TMY2 data files are the same as the ones in NSRDB, from which the TMY2 files were derived. However, differences do exist for data that were missing in the NSRDB, but then filled while developing the TMY2 data sets. Uncertainty values apply to the data with respect to when the data were measured, and not as to how "typical" a particular hour is for a future month and day. More information on data filling and the assignment of source and uncertainty flags is found in the TMY2 User’s Manual (Marion and Urban 1995).

Table A.2 TTMY2data .	TMY2 data records

| Field Position | Element | Values | Definition |
| --- | --- | --- | --- |
| 002 - 009 002 - 003 004 - 005 006 - 007 008 - 009 | Local Standard Time Year Month Day Hour | 61 - 90 1 - 12 1 - 31 1 - 24 | Year, 1961-1990 Month Day of month Hour of day in local standard time |
| 010 - 013 | Extraterrestrial Horizontal Radiation | 0 - 1415 | Amount of solar radiation in Wh/m2 received on a horizontal surface at the top of the atmosphere during the 60 minutes preceding the hour indicated |
| 014 - 017 | Extraterrestrial Direct Normal Radiation | 0 - 1415 | Amount of solar radiation in Wh/m2 received on a surface normal to the sun at the top of the atmosphere during the 60 minutes preceding the hour indicated |
| 018 - 023 018 - 021 022 023 | Global Horizontal Radiation Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 1200 A - H, ? 0 - 9 | Total amount of direct and diffuse solar radiation in Wh/m2 received on a horizontal surface during the 60 minutes preceding the hour indicated |
| 024 - 029 024 - 027 028 029 | Direct Normal Radiation Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 1100 A - H, ? 0 - 9 | Amount of solar radiation in Wh/m2 received within a 5.7° field of view centered on the sun during the 60 minutes preceding the hour indicated |
| 030 - 035 030 - 033 034 035 | Diffuse Horizontal Radiation Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 700 A - H, ? 0 - 9 | Amount of solar radiation in Wh/m2 received from the sky (excluding the solar disk) on a horizontal surface during the 60 minutes preceding the hour indicated |
| 036 - 041 036 - 039 040 041 | Global Horiz. Illuminance Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 1300 I, ? 0 - 9 | Average total amount of direct and diffuse illuminance in hundreds of lux received on a horizontal surface during the 60 minutes preceding the hour indicated 0 to 1300 = 0 to 130,000 lux |
| 042 - 047 042 - 045 046 047 | Direct Normal Illuminance Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 1100 I, ? 0 - 9 | Average amount of direct normal illuminance in hundreds of lux received within a 5.7° field of view centered on the sun during the 60 minutes preceding the hour indicated. 0 to 1100 = 0 to 110,000 lux |
| 048 - 053 048 - 051 052 053 | Diffuse Horiz. Illuminance Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 800 I, ? 0 - 9 | Average amount of illuminance in hundreds of lux received from the sky (excluding the solar disk) on a horizontal surface during the 60 minutes preceding the hour indicated. 0 to 800= 0 to 80,000 lux |
| Field Position | Element | Values | Definition |
| 054 - 059 054 - 057 058 059 | Zenith Luminance Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 7000 I, ? 0 - 9 | Average amount of luminance at the sky's zenith in tens of Cd/m2 during the 60 minutes preceding the hour indicated. 0 to 7000 = 0 to 70,000 Cd/m2 |
| 060 - 063 060 - 061 062 063 | Total Sky Cover Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 10 A - F 0 - 9 | Amount of sky dome in tenths covered by clouds or obscuring phenomena at the hour indicated |
| 064 - 067 064 - 065 066 067 | Opaque Sky Cover Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 10 A - F 0 - 9 | Amount of sky dome in tenths covered by clouds or obscuring phenomena that prevent observing the sky or higher cloud layers at the hour indicated |
| 068 - 073 068 - 071 072 073 | Dry Bulb Temperature Data Value Flag for Data Source Flag for Data Uncertainty | -500 to 500 A - F 0 - 9 | Dry bulb temperature in tenths of °C at the hour indicated -500 to 500 = -50.0 to 50.0°C |
| 074 - 079 074 - 077 078 079 | Dew Point Temperature Data Value Flag for Data Source Flag for Data Uncertainty | -600 to 300 A - F 0 - 9 | Dew point temperature in tenths of °C at the hour indicated -600 to 300 = -60.0 to 30.0°C |
| 080 - 084 080 - 082 083 084 | Relative Humidity Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 100 A - F 0 - 9 | Relative humidity in percent at the hour indicated |
| 085 - 090 085 - 088 089 090 | Atmospheric Pressure Data Value Flag for Data Source Flag for Data Uncertainty | 700 - 1100 A - F 0 - 9 | Atmospheric pressure at station in millibars at the hour indicated |
| 091 - 095 091 - 093 094 095 | Wind Direction Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 360 A - F 0 - 9 | Wind direction in degrees at the hour indicated. ( N = 0 or 360, E = 90, S = 180,W = 270 ). For calm winds, wind direction equals zero. |
| 096 - 100 096 - 098 099 100 | Wind Speed Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 400 A - F 0 - 9 | Wind speed in tenths of meters per second at the hour indicated. 0 to 400 = 0 to 40.0 m/s |
| 101 - 106 101 - 104 105 106 | Visibility Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 1609 A - F, ? 0 - 9 | Horizontal visibility in tenths of kilometers at the hour indicated. 7777 = unlimited visibility 0 to 1609 = 0.0 to 160.9 km 9999 = missing data |
| 107 - 113 107 - 111 112 113 | Ceiling Height Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 30450 A - F, ? 0 - 9 | Ceiling height in meters at the hour indicated. 77777 = unlimited ceiling height 88888 = cirroform 99999 = missing data |
| Field Position | Element | Values | Definition |
| 114 - 123 | Present Weather |  | Present weather conditions denoted by a 10-digit number. See Appendix B in the User’s Manual for key to present weather elements. |
| 124 - 128 124 - 126 127 128 | Precipitable Water Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 100 A - F 0 - 9 | Precipitable water in millimeters at the hour indicated |
| 129 - 133 129 - 131 132 133 | Aerosol Optical Depth Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 240 A - F 0 - 9 | Broadband aerosol optical depth (broad-band turbidity) in thousandths on the day indicated. 0 to 240 = 0.0 to 0.240 |
| 134 - 138 134 - 136 137 138 | Snow Depth Data Value Flag for Data Source Flag for Data Uncertainty | 0- 150 A - F, ? 0 - 9 | Snow depth in centimeters on the day indicated. 999 = missing data |
| 139 - 142 139 - 140 141 142 | Days Since Last Snowfall Data Value Flag for Data Source Flag for Data Uncertainty | 0 - 88 A - F, ? 0 - 9 | Number of days since last snowfall. 88 = 88 or greater days 99 = missing data |
| FORTRAN Sample Format: (lX, 4I2, 2I4, 7 (I4, Al, I1), 2( I2, Al, Il), 2 (I4, Al, Il), l(I3, Al, Il), l ( I4, Al, Il), 2 (I3, Al, I1), l (I4, Al, Il), l (I5, Al, Il), l0Il, 3 (I3, Al, Il), l (I2, Al, Il)) C Sample Format: (%2d%2d%2d%2d%4d%4d%4d%1s%1d%4d%1s%1d%4d%1s%1d%4d%1s%1d%4d%1s%1d%4d%1s %1d%4d%1s%1d%2d%1s%1d2d%1s%1d%4d%1s%1d%4d%1s%1d%3d%1s%1d%4d%1s%1d%3d %1s%1d%3d%1s%1d%4d%1s%ld%51d%1s%1d%1d%1d%1d%1d%1d%1d%1d%1d%1d%1d%3d%1s %1d%3d%1s%1d%3d%1s%1d%2d%1s%1d) Note: For ceiling height data, integer variable should accept data values as large as 99999. |