Dear Sounghun Yun,

first with TYPE 9 you have to be careful if you don't want to interpolate you have to use

-1 for the  first data, for the second -2  and so on if you use always  -1 this will only effect the first

data you read in.

For the timestep if you have a large influence of the ventilation it is always better to simulate with smaller timesteps  like

e.g. 0.01 h  due to this will lead to a smaller amount of energy change in one timestep and this is important for convergence.

For the comis problem. This problem is solved with TRNFLOW.

you find more about TRNFLOW at http://www.trnsys.de/ts/english/softeng/floeng/floeng.htm

TRNFLOW is  COMIS integrated in TYPE56. the Thermal model and the airflow model are now linked

internally. A new internal solver was integrated in TYPE56 which makes the simulations much more stable.

This can be shown by the following example which might be interesting for you to see why

certain airflow simulations are likely to be unstable:

Example:

-outside 10 °C.  2 rooms one is heated to 20 °C the other is not heated starting with a temperature of 20 °C

-at time=0 you open all the openings marked in the picture below.

-interesting is now the temperature of the unheated (left zone) and the airflow

-at time=0 both temperatures left and right zone are  equal so you can neglect the height of the opening in the middle

the airflow is coming from the lower opening (left zone) to the higher opening (right zone).

-if the temperature of the unheated left zone is near 10 °C you can neglect the height of the lower opening at the left zone

the airflow then comes in from the lower opening on the right side and goes out to the opening in the middle

so the airflow changed the direction. This switch point used to confuse the old way of coupling Comis to TYPE56.

as you can see in the results below.

-the red curve is the temperature in the unheated zone

-the magenta curve is the air change rate. As you can see with the new solver it

goes down to 0 and then with the opposite direction goes up again. While with the old solver

at the switch point you get strange results.

-the blue curve is the number of iterations divided by 10. While with the TRNFLOW-Version the maximum iterations are only 10

with the old way of coupling Comis the number of iterations reaches for a long time period the maximum of 40 which where the limits in

this TRNSYS-simulation. So during all this time the solution found was not convergent, this explains the strange results for airflow and temperature in this time

in the right graph.

with kind regards,

your TRNSYS Hotline Team

T.Welfonder, M.Rudolph

--------------------------------------------------------------------------------------------------------------------

*  TRANSSOLAR Energietechnik GmbH

*  Curiestrasse 2

*  70563 Stuttgart

*  Germany

*

*  Tel: 49 (0)711 67976-0

*  FAX: 49 (0)711 67976-11

*

*  Mailto:Hotline@transsolar.com

*  http://www.transsolar.com

*  http://www.trnsys.de

--------------------------------------------------------------------------------------------------------------------

New: TRNSYSlite 3.0 		more information about TRNSYSlite30 can be found at:	 http://www.trnsys.de/ts/english/softeng/tliteeng/tliteeng.htm.

--------------------------------------------------------------------------------------------------------------------

TRNSYS16     			more information about TRNSYS16 can be found at:    	 http://www.trnsys.de/ts/english/softeng/trneng/trneng.htm.

--------------------------------------------------------------------------------------------------------------------

TRNFLOW  			more information about TRNFlow can be found at: 		 http://www.trnsys.de/ts/english/softeng/floeng/floeng.htm .

--------------------------------------------------------------------------------------------------------------------

if you need any further information please contact hotline@transsolar.com.

-----Ursprüngliche Nachricht-----

Von: owner-trnsys@relay.doit.wisc.edu [mailto:owner-trnsys@relay.doit.wisc.edu] Im Auftrag von Sounghun Yun

Gesendet: Dienstag, 25. Mai 2004 06:22

An: trnsys@relay.doit.wisc.edu

Betreff:

Hi, every trnsys users.

I found some trouble from the result of Comis/Trnsys coupling calculation when there were severe indoor-outdoor temperature differences.  That is, when the indoor-outdoor temperature difference changed for a time step (changing about 3 or 5 degree

C for 1 hr), the amount of infiltration of building falling down unreasonably.  Generally speaking, if there was no wind around a building, the amount of infiltration of a building should have to be the smallest value when the indoor-outdoor temperature differences become zero.  And, I confirmed this like

result from the calculation of Comis stand-alone (single zonal mode and multi zonal model, too). Indeed, I handled the weather data to be no wind speed and the outdoor temperature should be changed step by step (for eg., 15 degree C for 12 hours and 20 degree C for the next 12 hours, etc.

And the indoor temperature is set to 20 degree C) for the purpose of finding some clue.  And the unreasonable value was found at the time when the temperature difference changed.  I have one more question in here ; why the output data is interpolated even though Type9 was set not to interpolate any input value(I entered "-1" for the setting of interpolation)? The problem was occurred at the time step of interpolation. When I set the simulation time step of control cards to be smaller(for eg. 10 minute), the results showing better than large time step(1hr).  Is there any relationship between the time step and Trnsys-Comis coupling?

Any one who has good idea about these problems, teach me please..

Best regards

****************************************************************

below : an example

Tin(C) Tout(C) infiltraion(m3/h)

3:00   20     10        40

4:00   20     10        40

5:00   20    12.5        6    <-- I entered 10 degree C for 5:00

6:00   20     15        30

7:00   20     15        30

****************************************************************